DIVISION 13

SPECIAL CONSTRUCTION SECTION 13200

PETROLEUM STORAGE TANK SYSTEMS

1.1   SCOPE OF SECTION

A.     This section describes requirements for providing the equipment, labor and materials necessary to furnish and install petroleum storage tank system[s] utilizing an aboveground steel tank[s] with secondary containment.

B.     Requirements include furnishing and installing all equipment and accessories necessary to make complete systems for the storage and dispensing of petroleum fuel.

C.     The following components shall be provided by the Owner and installed by the Contractor. [List if applicable]

D.     The following components shall be provided by the Contractor, but not be installed as a part of this contract. [List if applicable]

1.2   RELATED SECTIONS

A.     All material and installation sections relating to site preparation, painting, concrete and other related work not specified herein are covered in appropriate sections of this Specification.

B.     [List section titles and numbers]

1.3   DEFINITIONS

A.     AGREEMENT consists of the conditions of the contract between the Owner and the Contractor, including referenced specifications, drawings and related documents.

B.     AUTHORITY HAVING JURISDICTION is the [local fire marshal] [building official] [health department] [electrical inspector] [other] having statutory jurisdiction over the project.

C.     CONSTRUCTION DOCUMENTS consist of the general and supplemental conditions, specifications, drawings, and any addenda issued prior to bidding.

D.     CONTRACTOR is the person, firm, or corporation with whom Owner has entered into the Agreement.

E.     FURNISH means the Contractor shall supply the item specified, at the job site, unloaded, and secured against damage, vandalism or theft.

F.     FRP is an abbreviation for fiberglass reinforced plastic.

G.     INSTALL means the Contractor shall perform all work required to place the equipment specified in operation, including installation, testing, calibration, and start-up.

H.     INTERSTITIAL refers to the space between primary and secondary containment of tanks as well as piping.

I.     LEAK MODE TESTING refers to testing the integrity of the tanks and in accordance with the test device manufacturer's instructions and U.S. EPA Technical Standards.

J.     LIQUID TIGHT means prevention of the release of product from contained spaces into the surrounding soil and the prevention of infiltration of ground or surface water into a contained space.

K.     OWNER is the person or entity identified as such in the Agreement.

L.     PRODUCT means the [gasoline] [diesel] [fuel oil] [used oil] [other] stored and dispensed from the tank.

M.     PROVIDE means the Contractor shall Furnish and Install the equipment specified, and perform all work necessary to provide a complete and functional system.

N.     SPOIL means all material removed by demolition or excavating.

O.     STI is the Steel Tank Institute 570 Oakwood Drive, Lake Zurich, IL. 60047. (847) 438-8265

P.     SUBSTANTIAL COMPLETION is the stage in the progress of the Work when the Work or designated portion thereof is sufficiently completed in accordance with the Contract Documents for the Owner to utilize the Work for its intended use.

Q.     WORK means all materials, equipment, construction and services required by the Contract, whether completed or partially completed.

1.4   GENERAL REQUIREMENTS

A.     Unless otherwise specified, equipment furnished under this section shall be fabricated and installed in compliance with the instructions of the manufacturer.

B.     The Contractor shall ensure that all equipment, accessories and installation materials comply with the specification and that adequate provision is made in the tank design and fabrication for mounting the specified system equipment and accessories.

C.     The Contractor is solely responsible for construction means, methods, techniques, sequences and procedures and for safety precautions and programs.

D.     The contractor shall provide all labor, equipment and material required to provide a complete and functional system.

E.     To avoid delays in construction, the Contractor shall ensure that all components of the system are available at the time of installation.

F.     The Contractor shall coordinate his work with other work being performed at the construction site and minimize interference with the Owner's normal activities which may continue during construction.

G.     The Contractor shall obtain necessary permits, arrange for inspections and obtain approval of the appropriate Authority Having Jurisdiction over the work described.

1.5   STANDARDS

A.     The manufacture and installation of aboveground storage tank systems described in this section shall adhere to the following standards and regulatory requirements:

1.   Standard for Steel Aboveground Tanks for Flammable and Combustible Liquids, Standard UL 142; Control Equipment for Use With Flammable Liquid Dispensing Devices, UL 1238; Pipe Connectors for Flammable and Combustible Liquids and LP-Gas, UL 567; Powered-operated Dispensing Devices for Petroleum Products, UL 87; Valves for Flammable Fluids, UL 842; UL Listed Non-Metal Pipe, UL 971; Underwriters Laboratories Inc., 333 Pfingsten Road, Northbrook, Illinois 60062. (847) 272-8800.

2.  Recommended Practices for Installation of Aboveground Storage Systems for Motor Vehicle Fueling, PEI/RP200; Recommended Practices for Installation and Testing of Vapor Recovery Systems at Vehicle Fueling Sites, PEI/RP300; Petroleum Equipment Institute, P.O. Box 2380, Tulsa, OK 74101.

3.  Installation of Underground Petroleum Storage Systems, API/1615, American Petroleum Institute, 1220 L Street, Washington, D.C. 20005.

4.  Protected Aboveground Tanks for Motor Vehicle Fuel Dispensing Stations Outside Buildings, Article 79, Uniform Fire Code, 2000, International Fire Code Institute, 5360 Workman Mill Road, Whittier, California 90601-2298.

5.    Control of External Corrosion of Submerged Metallic Piping Systems, NACE Recommended Practice RP0169, External Catholic Protection of On-Grade Metallic Storage Tank Bottoms, NACE Recommended Practice RP0193-93, NACE International, P.O. Box 218340, Houston, TX 77213.

6.    Standard for Aboveground Tanks with Integral Secondary Containment, F-921®; Shop Fabricated Stationary Aboveground Storage Tanks for Flammable, Combustible Liquids - Installation Instructions, R912-00; Recommended Practice for Corrosion Protection of Underground Piping Networks Associated with Liquid Storage and Dispensing Systems, R892; Recommended Practice for External Corrosion Control of Shop Fabricated Aboveground Tank Floors, R893-98; Standard for Inspection of In-Service Shop Fabricated Aboveground Tanks for Storage of Combustible and Flammable Liquids, SP-001-00, Steel Tank Institute, 570 Oakwood Road, Lake Zurich, IL 60047 (847) 438-8265.

7.    Flammable and Combustible Liquids Code, NFPA 30, 1996, National Fire Protection Association, 1 Battery march Park, Quincy, Massachusetts 02269-9101.

8.    Automotive and Marine Service Station Code, NFPA 30A, 1996, National Fire Protection Association, 1 Batterymarch Park, Quincy, Massachusetts 02269-9101.

9.    National Electric Code, NFPA 70, 1993, National Fire Protection Association, 1 Batterymarch Park, Quincy, Massachusetts 02269-9101.

10.   National Fire Prevention Code, 1994, Building Officials and Code Administrators, 4051 Flossmoor Road, Country Club Hills, Illinois 60478.

11.   Standard Fire Prevention Code, 1995, Southern Building Code Congress International, 900 Montclair Road, Birmingham, Alabama 35213-1206.

12.  Occupational Safety and Health Standards, particularly Flammable and Combustible Liquids, 29CFR 1910.106, Personal Protective Equipment 29CFR 1910 Subpart I, Excavations 29CFR 1926.650 Subpart P, U. S. Department of Labor, Occupational Safety and Health Administration (OSHA), Washington, D.C.

13.    Clean Water Act and Oil Pollution Act of 1990, Spill Prevention, Control and Countermeasure (SPCC) Plans, 40 CFR 112, 113 and 114.

14.    Uniform building Code, International Conference of Building Officials, 5360 Workman Mill Road, Whittier, California 90601-2298.

15.    Applicable state and local regulations and ordinances

B.     In case of differences between building codes, state laws, local ordinances, utility company regulations, and contract documents, the most stringent shall govern.

C.     The codes and standards listed are the latest as of this publication.  Codes and standards are continuously updated. The Contractor shall confirm the construction standard edition enforced by the authority having jurisdiction.

1.6   SUBMITTALS

A.     The Contractor shall provide three (3) sets of shop drawings of the following system components for approval before commencing construction.

1.    Shop drawings of the tank(s) by the tank manufacturer.

2.    Assembly and installation drawings.

3.    Other. [List]

B.     The Contractor shall provide product data sheets and descriptive material for major components to be provided.

1.    Tank coatings.

2.    Pumps, valves and fittings.

3.    Piping, venting equipment, leak detection equipment, and overfill prevention equipment.

4.    Other system accessories. [List]

C.     Submittals shall be delivered to the Engineer within [10 days] of notice to proceed. The Engineer shall review the drawings and return them to the Contractor approved, or with appropriate comments, within [14 days] of receipt.

1.7   CONSTRUCTION DOCUMENTATION

A.     At contract close-out, the Contractor shall provide three (3) sets of the following installation instructions:

1.    Tank(s)

2.    Pumps, [dispensers], valves and fittings

3.    Vapor recovery components

4.    Other [List]

B.     The Contractor shall provide three (3) sets of manufacturers' system component operation and maintenance manual instructions.

C.     The Contractor shall provide record ("as-built") drawings and photographs of the following:

1.    All underground system components.

2.    The completed tank system in place.

D.     The Contractor shall provide copies of all testing and inspection reports to the Owner prior to substantial completion.

1.8   GUARANTEES, WARRANTIES AND INSURANCE

A.     The Contractor shall provide the following insurance [List type and limits]

B.     The Contractor shall provide the following guarantees/warranties [List requirements]

END OF SECTION

PART 2--PRODUCTS

2.1   SECONDARY CONTAINMENT ABOVEGROUND STORAGE TANK(S) (Tank 1)

A.    The storage tank(s) shall be F921® aboveground tank(s) for the storage of petroleum product(s) at near atmospheric pressure.  Number, size(s) and weight(s) of tank(s) shall be as follows.

(1)  3,000 gallon capacity (nominal) Horizontal Cylindrical tank for petroleum storage

Dimensions to be (diameter, length) 65 in., 221 in.

1.    The primary and secondary tanks shall be manufactured in accordance with Steel Tank Institute Publication No. F-921®, "Standard for Aboveground Tanks with Integral Secondary Containment."

2.    The tank shall consist of an inner steel wall and an outer steel wall.

3.    The inner and outer steel wall shall be UL 142 construction capable of providing containment of the primary storage tank's content.

4.    A legible UL 142 and Steel Tank Institute label shall be affixed to the side of the aboveground storage tank(s).

5.    Steel outer wall of the tank shall be coated to prolong weather resistance and to further reduce maintenance needs.

6.    The storage tank and supports shall be delivered as a complete UL listed unit.

7.    The storage tank and supports shall meet all the requirements for Seismic Zone 2b per Uniform Building Code requirements.

8.     Approved Manufactures:  General Industries, Inc., PO Box 1279 Goldsboro, NC, 27530.  www.gitank.com

9.  Approved equal must be approved by engineer 30 days prior to bid date.

10.  Manufacturer must have certified ISO 9001 quality system in place 60 days prior to award.

B.     Tank(s) shall be designed for use aboveground and include integral secondary containment.

C.     The [Contractor] [Owner] shall register each tank and serial number with Steel Tank Institute in accordance with instructions provided by the manufacturer with the tank.

E.     Tank(s) shall be provided with an [diameter]" diameter manway to allow access into tank(s).

F.     Provide an interstitial monitoring tube for monitoring the tank's interstice for liquids.

G.     Provide an external ladder [safety platform/catwalk] to allow access to top of tank for filling and maintenance that complies with applicable OSHA standards and building codes.

2.2   VENTING REQUIREMENTS

A.     Provide one (1) normal atmospheric or pressure/vacuum vent for the primary tank(s).

1.    Vents shall discharge upward or laterally, be protected from intrusion of rain [, and incorporate a flame arrestor.]

2.    When applicable, tanks located in Stage II Vapor Recovery mandated air quality areas shall be provided with pressure/vacuum vents.

3.    Vents for tanks containing Class 1 liquids shall terminate at least 12 feet above ground level and be located at least five feet from building openings.

4.    Vent installation shall comply with applicable sections of the fire and mechanical codes, including, but not limited to, NFPA 30A (2-4.5. e), NFPA 30 (2-3.5), or UFC (7902.1.10).

5.    Accepted manufacturers and part numbers: [List]

B.     Provide one (1) emergency vent for each primary tank or primary tank compartment.

1.    Vent size shall be determined by the tank configuration, the primary tank capacity, and the product stored.

2.    Emergency venting shall comply with provisions of NFPA 30A (2-4.5. f), NFPA 30 (2-3.6), or UFC (7902.2.6).

3.    Accepted manufacturers and part numbers: [List]

C.     Provide one (1) emergency vent for each secondary containment tank interstice.

1.    The venting capacity is determined by the tank configuration, secondary tank capacity, and the product stored.

2.    Emergency venting shall comply with provisions of NFPA 30A (2-4.5), NFPA 30 (2-3.6), or UFC (7902.2.6) (Article 79 5.3), and UL 142.

3.    Vents shall be located as close to the center of the tank as possible.

4.    Accepted manufacturers and part numbers: [List]

2.3   TANK FILLING AND OVERFILL PREVENTION COMPONENTS

A.     For tank(s) with [remote] [side] fill assembly, provide a lockable dry break adapter, lid, or check valve and quick connect coupling for each tank.

1.    Protect remote fills from physical damage, tampering and vandalism.

2.    Comply with provisions of NFPA 30 (2-4.6), NFPA 30A (2-4.9.4) or UFC Article 79 (5.6).

3.    Anti-siphon valve shall be provided for all remote fill or low mounted pump applications, in accordance with NFPA 30A (2-4.6.2 and 2-4.6.3); or UFC Article 79 (6.4); or BOCA (F-3207.5.6).  Anti-siphoning may be met by modifying the drop tube, piping or by installation of an electric solenoid valve.

[4.    Provide a Stage I vapor recovery system to capture displaced vapors during tank filling process.]

B.     Provide a spill container with cover and lockable hasp to contain product spills from the fill hose.  Spill containment shall comply with UFC Article 79 (5.7).

1.    Fill pipe spill container shall have a capacity of not less than five gallons.

2.    Provide a means for returning collected product to the storage tank (Not applicable to remote or side fill).

C.     Provide overfill prevention equipment which complies with the requirements of NFPA 30A (2-4.6.1) and which incorporates the following features:

1.    An audible alarm which will sound when the product level in the tank has reached 90% of tank capacity.

[2.    A positive shut-off fill limiter which will stop the flow of liquid into the tank when product level reaches 95% of tank capacity.]

[3.    The limiting device shall be rated to accept the fill flow rate and pressure.]

4.    Acceptable Manufacturers: [List]

D.     The Contractor shall provide a means for determining the liquid level in tank which is accessible to the delivery operator, in accordance with NFPA 30A (2-4.6.1) or UFC Article 79 (5.5).

2.4   MONITORING AND GAUGING SYSTEM

A.     Provide leak detection for each tank interstice to continuously monitor both the primary and secondary containment tanks.

B.     Probe shall be installed in each storage tank's interstitial monitoring tube.  The location of the monitoring console and external alarms are noted on the engineering drawings.

C.     Provide one (1) electronic tank gauging and monitoring system with the following features:

1.    Tank probe(s) for liquid level sensing

2.    Control console with display and printer

3.    Means of water detection

4.    External communications capabilities

5.    Tank liquid level and water measurement

D.     Provide an audible weather-proof alarm horn tied into the overfill monitoring system, which will be programmed to alarm as the tank contents reach a predetermined level, dictated by applicable codes.  Alarm must be located so that the person filling the tank can hear the alarm and halt the tank filling procedure.  Provide all associated conduit and wiring tied into the monitoring system located at [location].

E.     Storage tank to be manufactured by General Industries, Inc., Goldsboro, NC 919-751-1791. www.gitank.com

2.5   PIPING (As Applicable)

A.   Aboveground piping shall be Schedule 40 steel pipe with standard (150#) nodular iron fittings.

1.    Exposed piping shall be protected from exposure to outdoor conditions.

2.    Low melting point materials may be not be used aboveground.

2.6   VALVES, FITTINGS AND FLEXIBLE CONNECTORS

A.     Provide a [fire impact valve] [shear section] on product pipe beneath each dispenser. Model [list]

B.     Provide all-steel flexible connectors at dispenser connections as shown in the drawings. [Flexible connectors may not be required for system with flexible piping systems]

1.  Provide all-steel construction with a UL-listing for use aboveground (UL567).  Do not use connectors with low melting point materials.

[a. Flexible connectors for suction piping shall be rated for full vacuum service at 760mm Hg (mercury) vacuum.]

2.  Flexible connectors shall have one swivel end and one female pipe thread end. Units shall be clearly marked with a lay line to minimize chances of twisting during installation.

3.  Flexible connectors installed with a 90-degree bend shall be not less than [24] [30] - inches long.

4.  Acceptable manufacturers are: [list]

C.     Provide corrosion control using cathodic protection or isolation boots for each flexible connector in contact with the soil.

1.  Isolation boots shall completely isolate the metallic flexible connectors from the soil.

2.  A liquid-tight seal which can be tested at not less than 10 psig.

3.  Seal to FRP piping with at least two stainless steel hose clamps per end. Coat buried clamps with dielectric material after installation.

4.  Acceptable manufacturers are: [list]

D.     Provide a steel or nodular iron block valve to allow the tank and piping to be isolated and secured.

E.     Provide an anti-siphon device in the product piping at the tank which will prevent the flow of liquid from the tank unless the suction pump is operating, in accordance with NFPA 30A (2-4.6.2 and 2-4.6.3); UFC Article 79 (6.4); BOCA (F-3207.5.6).  Anti-siphoning may be met by installation of an electric solenoid valve.  A solenoid valve used in conjunction with an under-pump vacuum operated valve meets this requirement.

F.     Provide a pressure relief valve in each segment of blocked piping which will relieve excessive pressure resulting from thermal expansion and return any excess product to the tank.

G.     Provide portable Class ABC [20 pound] [40 pound] fire extinguisher(s) and weather proof cabinet(s) at dispenser island(s) and [other locations] in accordance with applicable fire codes.

H.     Provide [quantity] [size] diameter ["U" shaped steel pipe guards] [bollards] to be placed at the ends of the pump island, primed and painted.

2.7   PUMPING EQUIPMENT, VALVES AND FITTINGS--FUEL DISPENSING APPLICATIONS

A.     Provide a UL-Listed electric consumer pump with meter, hose and nozzle, low-mounted as indicated on drawing. Assembly shall be in full accordance with (NFPA 30A), or (UFC 5202), or (BOCA F-3207).

1.    The dispenser and its components shall be Underwriters Laboratories listed for the purpose intended.

2.    The dispenser shall comply with the requirements of NFPA 30A (4-2.5, 4-2.7), or UFC (5201 & 5202) or BOCA (F-3201.1 and 3207).

B.     Unless the suction pump is located directly in a tank opening, provide a listed, vacuum-actuated shut-off valve with a shear section. The valve shall be installed in strict accordance with the manufacturer's instructions.

1.   The valve shall be installed directly under dispenser and anchored to the dispenser with the shear section at the same level as the top of the island on which the suction pump is located in accordance with NFPA 30A (2-4.6.5), or UFC (5202.5.3.2); or BOCA (F-3205.9).

2.   Provide an electrically operated pressure regulating valve at the tank supply outlet which will operate simultaneously with the suction pump motor. The valve should not require backpressure to operate.

a.    Acceptable valve is [List].

3.    Provide the necessary mounting parts and piping in accordance with NFPA30A (2-4.6.6), or UFC (5201 and 5202).

[C.     Provide a Stage II vapor recovery system approved for use with aboveground tank systems by the California Air Resources Board, NFPA 30A (4-4 & 4-5) or UFC (5202.12).]

2.8   PUMP CONTROLS

A.     Provide an interface between the liquid sensing system and the pump power which will interrupt power to the pump if the high-level liquid sensor located in the containment sump senses the presence of liquid.

1.    The system is designed to force recognition of an unacceptably high level of water or released product in contained spaces and to prevent unauthorized restoration of power to the pumps in the event of a shut down.

2.    The relays shall be located in the [location].

B.     Provide electrical disconnection of all conductors to the pump in accordance with NFPA Codes 30, 30A and 70.

1.    Locate the emergency shut-off in an accessible area, at least 20 feet but not more than 100 feet from the dispenser.  Confirm the final location with the Owner prior to installation.

2.    Provide a palm type switch button that will shut off electrical power to the pump.

3.    The emergency shut-off shall be clearly identified with signage.

4.    Emergency shut-off shall have a manual reset.

END OF SECTION

PART 3--EXECUTION

3.1   GENERAL

A.  Familiarity with the Site.

1. Contractor shall familiarize himself with the location of all public utility facilities and structures that may be found in the vicinity of the construction.

2.  The Contractor shall conduct his operation to avoid damage to the utilities or structures. Should any damage occur due to the Contractor's operations, repairs shall be made at the Contractor's expense in a manner acceptable to the Owner.

3.  The Contractor is responsible for meeting all the requirements established by the agencies for utility work, as well as work affecting utilities and other government agencies.

3.2   SITE PREPARATION

A.   The site shall be prepared to ensure adequate support for the tank system and drainage of surface water.

1.    The foundation and tank supports shall be capable of supporting the weight of the tank and associated equipment when full.

2.    The foundation may be comprised of concrete, asphalt, gravel or other stable material designed to prevent tank movement, and must be rated for the seismic zone noted in Section 2.1 A 7 for each tank.

B.   Diking may not be required for F921® tanks of 12,000 gallon capacity and smaller.

1.    Regional and local fire codes authorities shall be consulted for local requirements.

2.    Notify the Engineer of any local requirements not incorporated in the system as designed.

C.   Provide a chain link fence at least 6 feet high, separated from the tanks by at least 10 feet and having a gate that is properly secured against unauthorized entry. (NFPA 30A, 2-4.7.1)

1.     Regional and local fire codes authorities shall be consulted for local requirements.

2.    Fencing at the tank area is not required by NFPA if the property on which the tanks are located is secured with a perimeter security fence.

D.   Provide barriers around aboveground tanks to protect the tank(s) against vehicular collision in accordance with fire regulations and building codes.  NFPA 30A (2-4.7.1) or BOCA (F-3205.4)

E.   Maintain legal separation distances from property lines, buildings, public ways, dispensers, vehicles being fueled and other storage tanks.

1.    Caution: Distance requirements vary significantly between jurisdictions.

2.    National standards dealing with set back and separation distances are included in NFPA 30A (2-4.2.2), or UFC Article 79 (5.1), or BOCA (F-3205.5 and F-3207.5.3).

3.3   TANK HANDLING, STORAGE AND INSTALLATION

A. Tanks shall be handled, lifted, stored and secured in accordance with the manufacturer's instructions.

B. Unload with equipment having sufficient lifting capacity to avoid damage to the tank. Securely store the tank at the job site.

C.   The tank and associated equipment shall be installed in accordance with the fire safety codes, regulations, standards and manufacturers instructions including:

1.    Federal, state and local fire safety, occupational health and environmental regulations.

2.    Steel Tank Institute installation instructions for F921® aboveground tanks (Publication No. R001-00, Installation and Testing Instructions for F921® Aboveground Storage Tanks).

3.    The installation instructions of other system component manufacturers.

4.    The Construction Documents and associated Drawings.

5.    Recommended Practices for Installation of Aboveground Storage Systems for Motor Vehicle Fueling, PEI/RP 200, Petroleum Equipment Institute.

D.   Advise the Owner of any shipping or handling damage encountered.

E.   No modifications shall be made to any tank without the prior written approval of the manufacturer and the Engineer.  This includes any welding on tank shells, adding penetrations in the tank structure, or repairing damage which might affect the integrity of the inner or outer tank.

3.4   CORROSION PROTECTION

A.   Any portion of the fueling system in contact with the soil shall be protected from corrosion in accordance with sound engineering practice and in accordance with NFPA 30A (2-4.8).

B.   Protect aboveground piping and equipment from corrosion by painting or wrapping it with a coating which is compatible with the product stored and the conditions of the exposure.

3.5   EXCAVATING AND TRENCHING (FOR REMOTE SYSTEMS W/ BURIED PIPING)

A.  Excavated materials.

1.  Contractor shall remove necessary paving by saw cutting and excavating as required to accomplish the work described on the drawings.

2.  Contractor shall temporarily stockpile excavated spoil on-site.  Contractor shall dispose of clean spoil [on-site] [off-site].

3.  Spoil shall not be considered acceptable as backfill.

3.6   BACKFILLING AND COMPACTION

A.  Contractor shall provide clean, pea gravel, compacted sand or crushed stone backfill for the foundation and/or product piping excavations.  All backfill material shall conform with ASTM standard C-33 paragraph 9.1.

1.  Pea gravel consisting of naturally-rounded particles with a minimum diameter of 1/8 inch and a maximum of 3/4 inch as backfill material.

2.  Washed crushed stone may be used if it is acceptable to the tank and pipe manufacturers. Crushed stone mix of angular particles with minimum size of 1/8 inch and maximum size of 1/2 inch.

3.  Sand shall be clean, well-granulated, free flowing, non-corrosive and inert.

4.  Provide laboratory analysis (sieve analysis) with pre-construction submittals. All materials must be approved in writing by the Engineer prior to placement.

B.  Contractor shall carefully place and compact the backfill around containment sumps, and piping.

C.  If dissimilar materials are used as backfill, or if the surrounding soil is unstable, separate the pea gravel or crushed stone backfill from the surrounding soil through use of geotextile filter fabric.

1.  Fabric strips must overlap by at least 18-inches, minimum thickness of 4 ounces per square yard.

2.  Acceptable filter fabric materials are [list].

3.7   EQUIPMENT INSTALLATION

A.  Contractor shall install tank(s), dispensers(s), piping and equipment in accordance with the manufacturers' installation instructions, industry standard recommended practices and federal, state and local regulations.

B.  Calibration and start-up of equipment shall be performed by factory-trained and qualified personnel.

C.  Pipe installation. (As Applicable)

1.  Maintain at least 1/8-inch slope in all pipe back to the tanks to prevent traps as prescribed in the standards.

2.  Provide at least two secondary pipe diameter clearance between parallel piping runs. Separate crossed piping by at least four-inches.

3.8   ELECTRICAL

A.  Installation of all electrical components including [list]:

B.  Installation shall be in accordance with manufacturers' installation instructions and shall conform to state and local electrical codes with special attention to compliance with requirements for work in classified areas.

C.  Provide explosion-proof electrical junction boxes, conduit and sealoffs specified in Article 500-514 of the National Electrical Code.

D.  Contractor shall provide wiring and seal-offs for all conduit.

3.9   CONCRETE

A.  Prior to setting the tanks in place, provide a grading plan showing final elevations and proposed location of control and expansion joints as a shop drawing.

B.  Contractor shall provide [6] [8] [10] -inch reinforced concrete paving for [tank] [fuel island area] pad as shown in the drawings.

1. [Provide 6 x 6 #6 WWF reinforcement] [Fiber mesh reinforcement].

2.  Miter all corners of pad.

C.  Provide an air entrained concrete mix design including plasticizer which will provide [2,000] [3,000] [4,000] psi strength after twenty-eight days, based on Department of Transportation standards for aggregate, mixing, testing, hardness, etc. Concrete mix to be approved by the Owner prior to paving.

D.  Frame out all street box openings during the general paving.

1.  Cast in all street boxes separately to ensure that the lids are set 1-inch above the general finished grade to inhibit infiltration of surface water.

2.  Provide dowels at joints of all street boxes as shown on plans.

3.  Provide diagonal reinforcement around all manholes as indicated on the drawings.

E.  Provide compacted backfill and concrete to match existing grades and surfaces.

F.  Use of additives for cold weather work must described in the mix design and subject to the approval of the Owner.

3.10   ASPHALTIC PAVING

A.  Asphalt pavement shall be replaced to a full depth of [4] [6] [8] inches.

B.  The existing asphalt pavement shall be sawcut for the entire depth and length of the new construction where full-depth asphalt pavement is to be placed.

C.  Materials

1.  Full depth asphalt material shall consist of two courses of [2] [3] [4] -inches each for a total depth of [4] [6] [8] -inches.

2.  Bottom course shall be a binder-type material as described in the DOT specifications. This course may be laid in full depth on compacted backfill and mechanically compacted and rolled.

3.  Top course shall be a surface-type mix put down and mechanically compacted or rolled in equal separate layers of 2-inches maximum each.

4.  All sub-grade areas receiving asphalt pavement, full-depth or resurfacing, shall be covered with a bituminous material prime coat as specified by DOT.

3.11   TESTING

A.  The Contractor is responsible for testing all installed systems for liquid tightness and proper operation, including:

1.  Pre-installation inspection of all materials.

2.  Product, containment and vent piping during construction.

3.  Containment sump integrity.

4.  System tightness test after all work, including paving, is completed and before the system is placed in service.

5.  Post installation inspection and testing eleven months after substantial completion of all work and approval of the Owner.

B.   Test each component of the system for calibration, tightness and proper operation in accordance with the instructions of the component manufacturer.

C.   Testing shall be documented by the Contractor and witnessed by the Engineer.

1.    Record the date and time of the test, the name of the tester and his affiliation with the project, and the names of each individual witnessing the test.

2.    Record the test method, duration and results.

3.    Provide a record of the testing to the Owner at the time of system start-up.

D.  Testing shall be witnessed by the Owner.

1.  The Owner shall witness tank delivery and setting in place, anchoring, piping backfilling, piping tests, final precision testing and system start-up.

2.  The Owner shall indicate approval of all testing witnessed in writing.

E.  Tests shall be performed in conformance with the manufacturers' instructions, state laws and the quoted industry standards, particularly PEI/RP200 and PEI/RP100.

1.  If a conflict exists between the test protocols, the most stringent test shall be performed.

2.  Any conflict which affects manufacturers' warranties must be resolved before beginning construction.

3.  The Contractor shall document all tests in writing, signed by the individuals who performed and witnessed the test.

F.  The Contractor shall demonstrate the operation of all systems to the Owner at the time of the final start-up test.

1.  Provide one day of instruction on the proper operation and maintenance of all components.

2.  Demonstrations shall include, but are not limited to, pump operation, monitoring and gauging systems, fuel filter replacement and leak detection.

3.12   TESTING PRIMARY AND SECONDARY TANKS

A.   Air pressure testing of the inner tank and secondary containment tank shall be conducted on-site, in the presence of the Engineer, before placing the tank in service.

B.    Refer to Publication No. R001-00 for complete procedural details.

C.    Other integrity tests may be required by the local authority having jurisdiction.

3.13   TESTING PRODUCT, CONTAINMENT AND VENT PIPING

A.  Test product and vent piping in accordance with manufacturer's instructions and quoted industry standards, particularly PEI/RP-100.

B.  Maintain minimum 10 psig pressure on all piping during backfilling and paving operations.

C.  Tightness test the piping at 50 psig before it is buried or connected to the tank. Soap and examine all connections for leakage.

D.  Tightness test the secondary containment piping with [5][10][20] psig before it is buried or connected to the tank. Soap and examine all connections for leakage.

3.14   TESTING CONTAINMENT SUMPS

A.  After piping and backfilling are completed, the Contractor shall perform a hydrostatic test on the containment sumps and manholes as follows:

1.  Fill the containment sump with water to a level near the top of the sump and above the penetration fittings. Mark liquid level on the sump wall.

2.  The test duration shall be at least 24 hours. Verify that the liquid level has not changed.

B.  If the water level changes, find and repair the leaks and repeat the test.

C.  After the test, remove all liquids, clean and dry the sumps.

D.  Monitor the sumps for liquid infiltration throughout completion of the remaining construction.

3.15   TEST DOCUMENTATION AND REPORTING

A.     The Contractor shall document all testing and provide copies to the Owner and authorities having jurisdiction. Test records shall include:

1.  Date and time of test.

2.  Name of tester.

3.  Names of any inspectors present.

4.  Test procedure followed.

5.  Test results.

B.  Provide documentation for all testing with contract close-out documentation to the Owner.

C.  The Contractor shall ensure that future testing is not impaired.  The Contractor may be requested to demonstrate the tests as a part of the final approval process.

1.  Inspection of tank interstices.

2.  Periodic hydrostatic testing of containment sump. Caution: Piping which has contained flammable or combustible liquids may not be air tested under any circumstances. (NFPA 30)

END OF SECTION