DIVISION 13

SECTION 13000

SINGLE WALL STEEL ABOVE GROUND STORAGE TANK

PART 1	GENERAL

1.1	SCOPE OF SECTION

1.1. A	This section describes requirements for providing the equipment, labor and materials necessary to furnish and install an above ground single wall steel tank.

1.1. B	Requirements include furnishing and installing all equipment and accessories necessary to make complete systems for the storage and dispensing of [list].

1.1.C	The following components shall be provided by the Owner and installed by the Contractor. [List if applicable]

1.2	GENERAL REQUIREMENTS

1.2. A	Unless otherwise specified, equipment furnished under this section shall be fabricated and installed in compliance with the instructions of the manufacturer.

1.2. B	The Contractor shall ensure that all equipment, accessories and installation materials comply with the specification and that adequate provision is made in the tank design and fabrication for mounting the specified system equipment and accessories.

1.2. C	The Contractor is solely responsible for construction means, methods, techniques, sequences and procedures and for safety precautions and programs.

1.2. D	The contractor shall provide all labor, equipment and material required to provide a complete and functional system.

1.2. E	To avoid delays in construction, the Contractor shall ensure that all components of the system are available at the time of installation.

1.2. F	The Contractor shall coordinate his work with other work being performed at the construction site and minimize interference with the Owner's normal activities which may continue during construction.

1.2. G	The Contractor shall obtain necessary permits, arrange for inspections and obtain approval of the appropriate Authority Having Jurisdiction over the work described.

1.3	DEFINITIONS

1.3. An	AGREEMENT consists of the conditions of the contract between the Owner and the Contractor, including referenced specifications, drawings and related documents.

1.3. B	AUTHORITY HAVING JURISDICTION is the [local fire marshal] [building official] [health department] [electrical inspector] [other] having statutory jurisdiction over the project.

1.3.C	CONSTRUCTION DOCUMENTS consist of the general and supplemental conditions, specifications, drawings, and any addenda issued prior to bidding.

1.3. D	CONTRACTOR is the person, firm, or corporation with whom Owner has entered into the Agreement.

1.3. E	FURNISH means the Contractor shall supply the item specified, at the job site, unloaded, and secured against damage, vandalism or theft.

1.3. F	INSTALL means the Contractor shall perform all work required to place the equipment specified in operation, including installation, testing, calibration, and start-up.

1.3. G	OWNER is the person or entity identified as such in the Agreement.

1.3. H	PRODUCT means the liquid stored in and dispensed from the tank.

1.3. I	PROVIDE means the Contractor shall Furnish and Install the equipment specified, and perform all work necessary to provide a complete and functional system.

1.3. J	SPOIL means all material removed by demolition or excavating.

1.3. K	SUBSTANTIAL COMPLETION is the stage in the progress of the Work when the Work or designated portion thereof is sufficiently completed in accordance with the Contract Documents for the Owner to utilize the Work for its intended use.

1.3. L	WORK means all materials, equipment, construction and services required by the Contract, whether completed or partially completed.

1.4	STANDARDS

1.4. A	The manufacture and installation of aboveground storage tank systems described in this section shall adhere to the following standards and regulatory requirements:

1.4.A.1		Standard for Steel Aboveground Tanks for Flammable and Combustible Liquids, Standard UL 142; Control Equipment for Use With Flammable Liquid Dispensing Devices, UL 1238; Pipe Connectors for Flammable and Combustible Liquids and LP-Gas, UL 567; Powered-operated Dispensing Devices for Petroleum Products, UL  87; Valves for Flammable Fluids, UL 842; UL Listed Non-Metal Pipe, UL 971; Underwriters Laboratories Inc., 333 Pfingsten Road, Northbrook, Illinois 60062. (847) 272-8800.

1.4. A.2	Recommended Practices for Installation of Aboveground Storage Systems for Motor Vehicle Fueling, PEI/RP200; Recommended Practices for Installation and Testing of Vapor Recovery Systems at Vehicle Fueling Sites, PEI/RP300; Petroleum Equipment Institute, P.O. Box 2380, Tulsa, OK 74101.

1.4. A.3	Flammable and Combustible Liquids Code, NFPA 30, 1996, National Fire Protection Association

1.4. A.4	Automotive and Marine Service Station Code, NFPA 30A, 1996, National Fire Protection Association

1.4. A.5	National Electric Code, NFPA 70, 1993, National Fire Protection Association.

1.4. A.6	National Fire Prevention Code, 1994, Building Officials and Code Administrators

1.4. A.7	Standard Fire Prevention Code, 1995, Southern Building Code Congress International

1.4. A.8	Occupational Safety and Health Standards, particularly Flammable and Combustible Liquids, 29CFR 1910.106, Personal Protective Equipment 29CFR 1910 Subpart I, Excavations 29CFR 1926.650 Subpart P, U. S. Department of Labor, Occupational Safety and Health Administration (OSHA), Washington, D.C.

1.4. A.9	Clean Water Act and Oil Pollution Act of 1990, Spill Prevention, Control and Countermeasure (SPCC) Plans, 40 CFR 112, 113 and 114.

1.4. A.10	Uniform Building Code ...

1.4. A.11	Applicable state and local regulations and ordinances

1.4. B	In case of differences between building codes, state laws, local ordinances, utility company regulations, and contract documents, the most stringent shall govern.

1.4. C	The codes and standards listed are the latest as of this publication. Codes and standards are continuously updated. The Contractor shall confirm the construction standard edition enforced by the authority having jurisdiction.

1.5	SUBMITTALS

1.5. A	The Contractor shall provide one (1) set of shop drawings of the following system components for approval before commencing construction.

1.5. A.1	1. Shop drawings of the tank(s) by the tank manufacturer.

1.5. A.2	2. Assembly and installation drawings.

1.5. A.3	3. Other. [List]

1.5. B	The Contractor shall provide product data sheets and descriptive material for major components to be provided.

1.5. B.1	1. Tank coatings.

1.5. B.2	2. Pumps, valves and fittings.

1.5. B.3	3. Piping, venting equipment, leak detection equipment, and overfill prevention equipment.

1.5. B.4	4. Other system accessories. [List]

1.5.C	C. Submittals shall be delivered to the Engineer within [10 days] of notice to proceed. The Engineer shall review the drawings and return them to the Contractor approved, or with appropriate comments, within [14 days] of receipt.

1.6	CONSTRUCTION DOCUMENTATION

1.6. A	At contract close-out, the Contractor shall provide three (3) sets of the following installation instructions:

1.6. A.1	1. Tank(s)

1.6. A.2	2. Pumps, [dispensers], valves and fittings

1.6. A.3	4. Other [List]

1.6. B	The Contractor shall provide three (3) sets of manufacturers' system component operation and Maintenance manual instructions.

1.6.C	The Contractor shall provide record ("as-built") drawings and photographs of the following:

1.6. C.1	1. All underground system components.

1.6. C.2	2. The completed tank system in place.

1.6. D	The Contractor shall provide copies of all testing and inspection reports to the Owner prior to substantial Completion.

1.7	GUARANTEES, WARRANTIES AND INSURANCE

1.7. A	The Contractor shall provide the following insurance [List type and limits]

1.7. B	The Contractor shall provide the following guarantees/warranties [List requirements]

PART 2	EQUIPMENT

2.1	SINGLE WALL STEEL ABOVEGROUND STORAGE TANK

2.1. A	The storage tank(s) shall be UL 142 aboveground tank(s) for the storage of petroleum product(s) at near atmospheric pressure.  Number, size(s) and weight(s) of tank(s) shall be as follows

2.1. A1         40,000 gallon capacity (nominal) Horizontal Cylindrical tank for petroleum storage    Dimensions to be (diameter, length) 144 in., 575 in.

2.1. A2          The tank shall be manufactured in accordance with UL 142.

2.1. A3          A legible UL 142 label shall be affixed to the side of the aboveground storage tank(s).

2.1. A4          Steel exterior of tank shall be coated to prolong weather resistance and further reduce maintenance needs.

2.1 A5           The storage tank and supports shall be delivered as a complete UL listed unit.

2.1 A6           The storage tank and supports shall meet all the requirements for Seismic Zone 2b per Uniform Building Code requirements

2.1. B

2.1. C

2.1. D

2.1. E

2.1. F

2.1. G	Approved Manufacturers

2.1. G.1	General Industries, Inc., PO Box 1279, Goldsboro, NC  27533, Phone:  919-751-1791, Website:  www.gitank.com

2.1. G.2	Approved Equal must be approved by engineer 30 days prior to bid date.

2.1. G.3 Manufacturer’s quality system shall be certified to ISO 9001.

2.2	Additional Information

2.2. A	The listed assembly shall meet the requirements for steel tanks as defined by NFPA 30.

2.2. B	Tank(s) shall be designed for use aboveground.

2.3	VENTING REQUIREMENTS

2.3. A	Provide one (1) normal atmospheric or pressure/vacuum vent for the primary tank(s).

2.3. A.1	Vents shall discharge upward or laterally, and be protected from intrusion of rain.

2.3. A.2	When applicable, tanks located in Stage II Vapor Recovery mandated air quality areas shall be provided with pressure/vacuum vents.

2.3. A.3	Vents for tanks containing Class 1 liquids shall terminate at least 12 feet above ground level and be located at least five feet from building openings.

2.3. A.4	Vent installation shall comply with applicable sections of the fire and mechanical codes, including, but not limited to, NFPA 30A (2-4.5. e) or NFPA 30 (2-3.5).

2.3. A.5	Accepted manufacturers and part numbers: [List]

2.3. B	Provide one (1) emergency vent for each primary tank or primary tank compartment.

2.3. B.1	Vent size shall be determined by the tank configuration, the primary tank capacity, and the product stored.

2.3. B.2	Emergency venting shall comply with provisions of NFPA 30A or NFPA 30.

2.3. B.3	Accepted manufacturers and part numbers: [List]

2.3. C.3	Vents shall be located as close to the center of the tank as possible.

2.3. C.4	Accepted manufacturers and part numbers: [List]

PART 3	EXECUTION

3.1	GENERAL

3.1. A	 Familiarity with the Site.

3.1. A.1	Contractor shall familiarize himself with the location of all public utility facilities and structures that may be found in the vicinity of the construction.

3.1. A.2	The Contractor shall conduct his operation to avoid damage to the utilities or structures. Should any damage occur due to the Contractor's operations, repairs shall be made at the Contractor's expense in a manner acceptable to the Owner.

3.1. A.3	The Contractor is responsible for meeting all the requirements established by the agencies for utility work, as well as work affecting utilities and other government agencies.

3.2	SITE PREPARATION

3.2. A	The site shall be prepared to ensure adequate support for the tank system and drainage of surface water.

3.2. A.1	The foundation and tank supports shall be capable of supporting the weight of the tank and associated equipment when full.

3.2. A.2	The foundation may be comprised of concrete, asphalt, gravel or other stable material designed to prevent tank movement, and must be rated for the seismic zone noted in Section 2.1 A 8 for each tank.

3.3	TESTING

3.3. A	The Contractor is responsible for testing all installed systems for liquid tightness and proper operation.

3.3. B	Test each component of the system for calibration, tightness and proper operation in accordance with the instructions of the component manufacturer.

3.3. C	Testing shall be documented by the Contractor and witnessed by the Engineer.

END OF SECTION