| DIVISION 13 |  |  |  |
| --- | --- | --- | --- |
| SECTION 13200 |  |  |  |
| STEEL TANK FOR RAIN WATER STORAGE |  |  |  |
| PART 1 - GENERAL |  |  |  |
| 1.1 | SCOPE OF SECTION |  |  |
|  | A. |  | This section describes requirements for providing the equipment, labor and materials necessary to furnish and install a XXXX gallon steel storage tank system for rain water storage. |
|  | B. |  | Requirements include furnishing and installing all equipment and accessories necessary to make a complete system for the storage and dispensing of non-potable water |
|  | C. |  | The following components shall be provided by the Owner and installed by the Contractor. [List if applicable] |
|  | D. |  | The following components shall be provided by the Contractor, but not be installed as a part of this contract. [List if applicable] |
| 1.2 | RELATED SECTIONS |  |  |
|  | A. |  | All material and installation sections relating to site preparation, painting, concrete and other related work not specified herein are covered in appropriate sections of this Specification. |
|  | B. |  | [List related section titles and numbers] |
| 1.3 | DEFINITIONS |  |  |
|  | A. |  | AGREEMENT consists of the conditions of the contract between the Owner and the Contractor, including referenced specifications, drawings and related documents. |
|  | B. |  | AUTHORITY HAVING JURISDICTION is the [local fire marshal] [building official] [health department] [electrical inspector] [other] having statutory jurisdiction over the project. |
|  | C. |  | CONSTRUCTION DOCUMENTS consist of the general and supplemental conditions, specifications, drawings, and any addenda issued prior to bidding. |
|  | D. |  | CONTRACTOR is the person, firm, or corporation with whom Owner has entered into the Agreement. |
|  | E. |  | FURNISH means the Contractor shall supply the item specified, at the job site, unloaded, and secured against damage, vandalism or theft. |
|  | F. |  | INSTALL means the Contractor shall perform all work required to place the equipment specified in operation, including installation, testing, calibration, and start-up. |
|  | G. |  | OWNER is the person or entity identified as such in the Agreement. |
|  | H. |  | PRODUCT means the liquid stored in and dispensed from the tank. |
|  | I. |  | PROVIDE means the Contractor shall Furnish and Install the equipment specified, and perform all work necessary to provide a complete and functional system. |
|  | J. |  | SPOIL means all material removed by demolition or excavating. |
|  | K. |  | SUBSTANTIAL COMPLETION is the stage in the progress of the Work when the Work or designated portion thereof is sufficiently completed in accordance with the Contract Documents for the Owner to utilize the Work for its intended use. |
|  | L. |  | WORK means all materials, equipment, construction and services required by the Contract, whether completed or partially completed. |
| 1.4 | GENERAL REQUIREMENTS |  |  |
|  | A. |  | Unless otherwise specified, equipment furnished under this section shall be fabricated and installed in compliance with the instructions of the manufacturer. |
|  | B. |  | The Contractor shall ensure that all equipment, accessories and installation materials comply with the specification and that adequate provision is made in the tank design and fabrication for mounting the specified system equipment and accessories. |
|  | C. |  | The Contractor is solely responsible for construction means, methods, techniques, sequences and procedures and for safety precautions and programs. |
|  | D. |  | The contractor shall provide all labor, equipment and material required to provide a complete and functional system. |
|  | E. |  | To avoid delays in construction, the Contractor shall ensure that all components of the system are available at the time of installation. |
|  | F. |  | The Contractor shall coordinate his work with other work being performed at the construction site and minimize interference with the Owner's normal activities which may continue during construction. |
|  | G. |  | The Contractor shall obtain necessary permits, arrange for inspections and obtain approval of the appropriate Authority Having Jurisdiction over the work described. |
| 1.5 | STANDARDS |  |  |
|  | A. |  | The manufacture and installation of aboveground storage tank systems described in this section shall adhere to the following standards and regulatory requirements: |
|  |  | 1. | Welded Carbon Steel Tanks for Water Storage, AWWA D-100, Coating Steel Water-Storage Tanks, AWWA D-102, American Water Works Association, 6666 West Quincy Ave., Denver, CO 80235-3098 |
|  |  | 2. | Welded Tanks for Oil Storage, API Standard 650, Eleventh Edition, June 2007, American Petroleum Institute, 1220 L Street NW, Washington, DC 20005 |
|  |  | 3. | Control of External Corrosion of Submerged Metallic Piping Systems, NACE Recommended Practice RP0169, ; External Catholic Protection of On-Grade Metallic Storage Tank Bottoms, NACE Recommended Practice RP0193-93, NACE International, P.O. Box 218340, Houston, TX 77213. |
|  |  | 4 | National Fire Prevention Code, 1994, Building Officials and Code Administrators, 4051 Flossmoor Road, Country Club Hills, Illinois 60478. |
|  |  | 5 | Standard Fire Prevention Code, 1995, Southern Building Code Congress International, 900 Montclair Road, Birmingham, Alabama 35213-1206. |
|  |  | 6 | Occupational Safety and Health Standards, particularly Flammable and Combustible Liquids, 29CFR 1910.106, Personal Protective Equipment 29CFR 1910 Subpart I, Excavations 29CFR 1926.650 Subpart P, U. S. Department of Labor, Occupational Safety and Health Administration (OSHA), Washington, D.C. |
|  |  | 7 | Clean Water Act and Oil Pollution Act of 1990, Spill Prevention, Control and Countermeasure (SPCC) Plans, 40 CFR 112, 113 and 114. |
|  |  | 8 | Uniform building Code, International Conference of Building Officials, 5360 Workman Mill Road, Whittier, California 90601-2298. |
|  |  | 9 | Applicable state and local regulations and ordinances |
| B. |  |  | In case of differences between building codes, state laws, local ordinances, utility company regulations, and contract documents, the most stringent shall govern. |
| C. |  |  | The codes and standards listed are the latest as of this publication. Codes and standards are continuously updated. The Contractor shall confirm the construction standard edition enforced by the authority having jurisdiction. |
| 1.6 | SUBMITTALS |  |  |
|  | A. |  | The Contractor shall provide three (3) sets of shop drawings of the following system components for approval before commencing construction. |
|  |  | 1. | Shop drawings of the tank(s) by the tank manufacturer. |
|  |  | 2. | Assembly and installation drawings. |
|  |  | 3. | Other. [List] |
|  | B. |  | The Contractor shall provide product data sheets and descriptive material for major components to be provided. |
|  |  | 1. | Tank coatings. |
|  |  | 2. | Pumps, valves and fittings. |
|  |  | 3. | Piping, venting equipment, leak detection equipment, and overfill prevention equipment. |
|  |  | 4. | Other system accessories. [List] |
|  | C. |  | Submittals shall be delivered to the Engineer within [10 days] of notice to proceed. The Engineer shall review the drawings and return them to the Contractor approved, or with appropriate comments, within [14 days] of receipt. |
| 1.7 | CONSTRUCTION DOCUMENTATION |  |  |
|  | A. |  | At contract close-out, the Contractor shall provide three (3) sets of the following installation instructions: |
|  |  | 1. | Tank(s) |
|  |  | 2. | Pumps, [dispensers], valves and fittings |
|  |  | 3 | Other [List] |
|  | B. |  | The Contractor shall provide three (3) sets of manufacturers' system component operation and maintenance manual instructions. |
|  | C. |  | The Contractor shall provide record ("as-built") drawings and photographs of all system components |
|  | D. |  | The Contractor shall provide copies of all testing and inspection reports to the Owner prior to substantial completion. |
| 1.8 | GUARANTEES, WARRANTIES AND INSURANCE |  |  |
|  | A. |  | The Contractor shall provide the following insurance [List type and limits] |
|  | B. |  | The Contractor shall provide the following guarantees/warranties [List requirements] |
| PART 2 - PRODUCTS |  |  |  |
| 2.1 |  |  | CAPACITY |
| 2.1.A |  |  | DIMENSIONS |
| 2.1.B |  |  | BOTTOM TYPE |
| 2.1.C |  |  | TOP TYPE |
| 2.1.D |  |  | SHELL MANWAYS |
| 2.1.E |  |  | TOP MANWAYS |
| 2.1.F |  |  | NPT CONNECTIONS |
| 2.1.G |  |  | FLANGED CONNECTIONS |
| 2.1.G |  |  | Approved Manufacturers |
| 2.1.G.1 |  |  | General Industries, Inc., PO Box 1279, Goldsboro, NC 27533, Phone: 919-751-1791, Website: www.gitank.com |
| 2.1.G.2 |  |  | Approved Equal must be approved by engineer 30 days prior to bid date. |
| 2.1.G.3 |  |  | Tank manufacturer shall be ISO 9001 certified. |
| 2.2 |  |  | Additional Information |
| 2.2.A |  |  | Tanks shall be double butt welded with full penetration welds. |
| 2.2.B |  |  | 3 coat exterior coating system shall be Exterior Coating System #6 as per AWWA D-102 |
| 2.2.C |  |  | 2 coat interior coating system shall be Interior Coating System #1 as per AWWA D-102. |
| 2.2.D |  |  | Tank shall have both a top and shell manway |
| 2.3 | VENTING REQUIREMENTS |  |  |
|  | A. |  | Provide one (1) normal atmospheric vent sized per the largest inlet or outlet connection. |
| PART 3 - EXECUTION |  |  |  |
| 3.1 | GENERAL |  |  |
|  | A. |  | Familiarity with the Site. |
|  |  | 1. | Contractor shall familiarize himself with the location of all public utility facilities and structures that may be found in the vicinity of the construction. |
|  |  | 2. | The Contractor shall conduct his operation to avoid damage to the utilities or structures. Should any damage occur due to the Contractor's operations, repairs shall be made at the Contractor's expense in a manner acceptable to the Owner. |
|  |  | 3. | The Contractor is responsible for meeting all the requirements established by the agencies for utility work, as well as work affecting utilities and other government agencies. |
| 3.2 | SITE PREPARATION |  |  |
|  | A. |  | The site shall be prepared to ensure adequate support for the tank system and drainage of surface water. |
|  |  | 1. | The foundation and tank supports shall be capable of supporting the weight of the tank and associated equipment when full. |
|  |  | 2. | The foundation may be comprised of concrete, asphalt, gravel or other stable material designed to prevent tank movement, and must be rated for the seismic zone noted in Section 2.1 A 7 for each tank. |
|  | B. |  | Regional Code Awareness |
|  |  | 1. | Regional and local fire codes authorities shall be consulted for local requirements. |
|  |  | 2. | Notify the Engineer of any local requirements not incorporated in the system as designed. |
|  | C. |  | Provide a chain link fence at least 6 feet high, separated from the tanks by at least 10 feet and having a gate that is properly secured against unauthorized entry. (NFPA 30A, 2-4.7.1) |
|  |  | 1. | Regional and local fire codes authorities shall be consulted for local requirements. |
|  |  | 2. | Fencing at the tank area is not required by NFPA if the property on which the tanks are located is secured with a perimeter security fence. |
|  | D. |  | Provide barriers around aboveground tanks to protect the tank(s) against vehicular collision in accordance with fire regulations and building codes. NFPA 30A (2-4.7.1) or BOCA (F-3205.4) |
|  | E. |  | Maintain legal separation distances from property lines, buildings, public ways, dispensers, vehicles being fueled and other storage tanks. |
|  |  | 1.1 | Caution: Distance requirements vary significantly between jurisdictions. |
| 3.3 | TANK HANDLING, STORAGE AND INSTALLATION |  |  |
|  | A. |  | Tanks shall be handled, lifted, stored and secured in accordance with the manufacturer's instructions. |
|  | B. |  | Unload with equipment having sufficient lifting capacity to avoid damage to the tank. Securely store the tank at the job site. |
|  | C. |  | The tank and associated equipment shall be installed in accordance with the fire safety codes, regulations, standards and manufacturer’s instructions including: |
|  |  | 1. | Federal, state and local fire safety, occupational health and environmental regulations. |
|  |  | 2. | The installation instructions of other system component manufacturers. |
|  |  | 3. | The Construction Documents and associated Drawings. |
|  | D. |  | Advise the Owner of any shipping or handling damage encountered. |
|  | E. |  | No modifications shall be made to any tank without the prior written approval of the manufacturer and the Engineer. This includes any welding on tank shells, adding penetrations in the tank structure, or repairing damage which might affect the integrity of the inner or outer tank. |
| END OF SECTION |  |  |  |